## input
HVAC Zone loads and Sizing Output
Sefaira Systems
Zone |  |  |  | Internal Conditions |  |  |  | Peak Cooling Design Day |  |  |  | Peak Heating Design Day |  |  |  | Peak Zone Cooling Load |  | Peak Zone Heating Load | Airflow |  |  | Coil Loads |  | Setpoints
Name | Floor | Area [m^2] | Type | Template | Lighting [W/m^2] | Occupancy [m^2/person] | Plug Loads [W/m^2] | Name | Day | Month | Time | Name | Day | Month | Time | Sensible [kW] | Latent [kW] | Sensible [kW] | Design Airflow [L/s] | Outside Airflow [L/s] | Minimum Outside Airflow [L/s] | Cooling Coil / Beam Design Load [kW] | Heating Coil / Radiator Design Load [kW] | Cooling [C] | Cooling RH | Heating [C] | Heating RH
L001_P01 | 1 | 44 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 09:00:00 | 1.6221 | 0.28195 | 1.7842 | 110.4031 | 35.2 | 35.2 | 1.6562 | 1.8655 | 24 | 50% | 21 | n/a
L001_P02 | 1 | 84 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 3.6881 | 0.57247 | 3.4527 | 218.4474 | 67.2 | 67.2 | 4.1144 | 3.3769 | 24 | 50% | 21 | n/a
L001_P03 | 1 | 72.9301 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 10:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 2.702 | 0.48274 | 3.2022 | 183.5026 | 58.344 | 58.344 | 3.002 | 3.2738 | 24 | 50% | 21 | n/a
L001_P04 | 1 | 93.0699 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 09:00:00 | 6.7679 | 0.75092 | 4.9463 | 411.8852 | 74.456 | 74.456 | 7.6805 | 5.4566 | 24 | 50% | 21 | n/a
L001_P05 | 1 | 58.2937 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 5.8933 | 0.43724 | 3.1899 | 385.6303 | 46.635 | 46.635 | 7.4998 | 3.1766 | 24 | 50% | 21 | n/a
L001_P06 | 1 | 48 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.5848 | 0.36121 | 2.6713 | 296.644 | 38.4 | 38.4 | 5.3977 | 2.6759 | 24 | 50% | 21 | n/a
L001_P07 | 1 | 54 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 10:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.3655 | 0.377 | 3.216 | 313.1357 | 43.2 | 43.2 | 5.0481 | 3.4913 | 24 | 50% | 21 | n/a
L001_P08 | 1 | 54 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 13:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 3.9705 | 0.3538 | 2.8638 | 278.0089 | 43.2 | 43.2 | 3.847 | 2.8247 | 24 | 50% | 21 | n/a
L001_P09 | 1 | 55.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 13:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.0117 | 0.35659 | 2.712 | 281.306 | 44.4 | 44.4 | 3.9058 | 2.6896 | 24 | 50% | 21 | n/a
L001_P10 | 1 | 62.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 13:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.1932 | 0.40013 | 3.0322 | 289.2772 | 50 | 50 | 3.9636 | 2.9672 | 24 | 50% | 21 | n/a
L001_P11 | 1 | 45.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.8457 | 0.32976 | 2.9087 | 352.0994 | 36.4 | 36.4 | 5.0198 | 2.9671 | 24 | 50% | 21 | n/a
L001_P12 | 1 | 35.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 3.7883 | 0.25963 | 2.3247 | 273.6858 | 28.4 | 28.4 | 3.8847 | 2.3973 | 24 | 50% | 21 | n/a
L001_P13 | 1 | 34 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 3.5199 | 0.23995 | 2.0617 | 252.4462 | 27.2 | 27.2 | 3.5659 | 2.1352 | 24 | 50% | 21 | n/a
L001_P14 | 1 | 515.7063 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 28.4901 | 3.65 | 24.6188 | 1582.0098 | 412.565 | 412.565 | 34.31 | 23.8797 | 24 | 50% | 21 | n/a
L001_P15 | 1 | 62 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 6.1486 | 0.48439 | 4.003 | 441.7624 | 49.6 | 49.6 | 6.3122 | 4.0078 | 24 | 50% | 21 | n/a
L002_P01 | 2 | 44 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 1.9429 | 0.28773 | 1.3785 | 116.5766 | 35.2 | 35.2 | 2.1074 | 1.4711 | 24 | 50% | 21 | n/a
L002_P02 | 2 | 84 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.1038 | 0.5786 | 2.5217 | 223.9609 | 67.2 | 67.2 | 4.1659 | 2.4239 | 24 | 50% | 21 | n/a
L002_P03 | 2 | 72.9301 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 10:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 3.1452 | 0.48974 | 2.5472 | 189.2476 | 58.344 | 58.344 | 3.2845 | 2.4844 | 24 | 50% | 21 | n/a
L002_P04 | 2 | 93.0699 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 10:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 6.757 | 0.73753 | 5.1316 | 465.3579 | 74.456 | 74.456 | 7.7755 | 4.9635 | 24 | 50% | 21 | n/a
L002_P05 | 2 | 58.2937 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 5.604 | 0.44049 | 2.6266 | 361.1539 | 46.635 | 46.635 | 6.4015 | 2.5134 | 24 | 50% | 21 | n/a
L002_P06 | 2 | 48 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 6) | 21 | Jun | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.4467 | 0.34812 | 2.201 | 290.4346 | 38.4 | 38.4 | 5.0417 | 2.1086 | 24 | 50% | 21 | n/a
L002_P07 | 2 | 54 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 13:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.4658 | 0.38292 | 3.0597 | 319.1869 | 43.2 | 43.2 | 4.9058 | 2.9503 | 24 | 50% | 21 | n/a
L002_P08 | 2 | 54 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 13:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 3.9582 | 0.35851 | 2.3305 | 278.0801 | 43.2 | 43.2 | 3.892 | 2.2358 | 24 | 50% | 21 | n/a
L002_P09 | 2 | 55.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 13:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.0307 | 0.3609 | 2.146 | 282.51 | 44.4 | 44.4 | 3.9301 | 2.0524 | 24 | 50% | 21 | n/a
L002_P10 | 2 | 62.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 13:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.2127 | 0.40488 | 2.3985 | 291.8903 | 50 | 50 | 4.0416 | 2.2989 | 24 | 50% | 21 | n/a
L002_P11 | 2 | 45.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.5637 | 0.33448 | 2.477 | 327.2905 | 36.4 | 36.4 | 4.5631 | 2.404 | 24 | 50% | 21 | n/a
L002_P12 | 2 | 35.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 3.5972 | 0.26347 | 1.9857 | 258.9869 | 28.4 | 28.4 | 3.6742 | 1.949 | 24 | 50% | 21 | n/a
L002_P13 | 2 | 515.7063 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 29.9695 | 3.6909 | 19.5257 | 1745.6573 | 412.565 | 412.565 | 32.3459 | 18.8182 | 24 | 50% | 21 | n/a
L002_P14 | 2 | 34 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 3.3675 | 0.24313 | 1.7265 | 240.7187 | 27.2 | 27.2 | 3.4072 | 1.6981 | 24 | 50% | 21 | n/a
L002_P15 | 2 | 62 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 5.8543 | 0.49285 | 3.5868 | 416.8608 | 49.6 | 49.6 | 6.0311 | 3.4451 | 24 | 50% | 21 | n/a
L003_P01 | 3 | 44 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 09:00:00 | 1.9451 | 0.289 | 2.1068 | 130.6706 | 35.2 | 35.2 | 2.053 | 2.2142 | 24 | 50% | 21 | n/a
L003_P02 | 3 | 84 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.5593 | 0.58417 | 3.6295 | 275.3281 | 67.2 | 67.2 | 4.5267 | 3.9485 | 24 | 50% | 21 | n/a
L003_P03 | 3 | 72.9301 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 09:00:00 | 3.4266 | 0.51036 | 3.4183 | 228.5535 | 58.344 | 58.344 | 3.7287 | 3.7771 | 24 | 50% | 21 | n/a
L003_P04 | 3 | 93.0699 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 7) | 21 | Jul | 10:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 09:00:00 | 6.6651 | 0.68387 | 5.6914 | 480.7714 | 74.456 | 74.456 | 8.5775 | 6.1216 | 24 | 50% | 21 | n/a
L003_P05 | 3 | 58.2937 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 5.8765 | 0.44426 | 3.373 | 380.8255 | 46.635 | 46.635 | 6.7054 | 3.6568 | 24 | 50% | 21 | n/a
L003_P06 | 3 | 48 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.8165 | 0.3674 | 2.8164 | 312.3818 | 38.4 | 38.4 | 5.5117 | 3.081 | 24 | 50% | 21 | n/a
L003_P07 | 3 | 54 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 13:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 09:00:00 | 4.4767 | 0.38636 | 3.602 | 317.6967 | 43.2 | 43.2 | 4.8677 | 3.8634 | 24 | 50% | 21 | n/a
L003_P08 | 3 | 54 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 14:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.015 | 0.36189 | 3.0203 | 281.2751 | 43.2 | 43.2 | 3.8692 | 3.2652 | 24 | 50% | 21 | n/a
L003_P09 | 3 | 55.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 13:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.0105 | 0.36313 | 2.8614 | 281.0041 | 44.4 | 44.4 | 3.9169 | 3.1329 | 24 | 50% | 21 | n/a
L003_P10 | 3 | 62.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS DB=>MWB (MONTH 9) | 21 | Sep | 14:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 4.2382 | 0.40818 | 3.2003 | 292.6296 | 50 | 50 | 3.9918 | 3.4212 | 24 | 50% | 21 | n/a
L003_P11 | 3 | 45.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 09:00:00 | 4.879 | 0.33739 | 3.0394 | 352.3044 | 36.4 | 36.4 | 5.0241 | 3.3303 | 24 | 50% | 21 | n/a
L003_P12 | 3 | 35.5 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 09:00:00 | 3.7731 | 0.26577 | 2.4629 | 271.6479 | 28.4 | 28.4 | 3.8742 | 2.6862 | 24 | 50% | 21 | n/a
L003_P13 | 3 | 515.7063 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 09:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 08:00:00 | 31.0684 | 3.7182 | 26.1118 | 1814.1294 | 412.565 | 412.565 | 32.989 | 26.866 | 24 | 50% | 21 | n/a
L003_P14 | 3 | 34 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 09:00:00 | 3.5335 | 0.24503 | 2.2839 | 253.521 | 27.2 | 27.2 | 3.6052 | 2.5024 | 24 | 50% | 21 | n/a
L003_P15 | 3 | 62 | Perimeter |  | 6 | 10 | 10 | 3600175 ANN CLG .4% CONDNS ENTH=>MDB | 21 | Jul | 18:00:00 | 3600175 ANN HTG 99.6% CONDNS DB | 21 | Jan | 09:00:00 | 6.2216 | 0.4981 | 4.0936 | 443.9149 | 49.6 | 49.6 | 6.3545 | 4.4428 | 24 | 50% | 21 | n/a